# BRIEFING NOTE

## Woodlands – South Marston Primary Street RMA Comments Tracker (27/05/25 Resubmission)

## 27 May 2025

This tracker provides a summary of consultee comments received in relation to the South Marston Primary Street amendments submitted 27th February 2025 and VTW’s proposed response / actions.  Full comments are located - S/RES/24/1020.

|  | Comments | Response / Actions |
| --- | --- | --- |
| LLFA (28-Apr-25) |  |  |
|  | Based on calculations provided in Appendix C of the drainage strategy report, during a rainfall event with the 1 in 100 years likelihood plus 40% CC, Nodes S17,S18,S19,S20 and S40 show flooding in excess of 30m3. Assuming the design criteria is the 1 in 30 year event, the 1 in 100 plus 40%CC is treated to be an exceedance event scenario. Despite the likely exceedance routes have been plotted on the proposed layout and included in Appendix B, but we need to know where the flood volume would go, pond and/or at what point will be directed to the natural ditches or man-made drainage system | The nodes referenced and flooding shown is outside of the application boundary. Flooding will be designed out through the inclusion of a full drainage network within each reserved matters phase upstream of this network, therefore flows will be managed within the SuDS and sewer network to the attenuation features in line with the overarching drainage strategy. |
|  | The drainage-related points raised in the South Marston Parish Council comments need to be addressed. | These comments have been addressed below. |
|  | SBC Landscape Architecture (26-Mar-25) |  |
|  | No objection. | No action required |
| SBC Highways (17-Mar-25) |  |  |
|  | Concern remains with the ability to safeguard bus stops, given the lack of restrictions proposed along the Primary Street. | Parking will be restricted along the Primary Street in the form of parking signs depicting clearway zones. The bus stop also has yellow box markings to prevent parking. Double yellow lines have not been proposed on SBC Highways Agreements advice, as they are difficult to enforce. No action required |
|  | The residential parcels R6 & R7 and R8 & R9 have now received reserved matters approval, and I would ask that these are shown on the plans. | Not essential for determination. No action required |
|  | Guidance provided in LTN 1/20, at Chapter 10, advises that the cycle crossings should be Parallel or Toucan Crossings. Having regard for the location of the bus stop near ‘Carpenters Walk,’ and the need for consistency along the Primary Street, colleagues in Traffic Management and Road Safety have advised that the preference would for Toucan Crossings. | Noting that LTN 1/20 is guidance and upon further consideration of expected traffic flows, toucan crossings are not considered justified in these locations. Discussions have also been held between Brookbanks and SBC’s Highways Agreement Team and it has been confirmed that the eastern zebra crossing (close to parcel R6 and R8) will have lower vehicle speeds due to the proximity of the residential parcels and therefore a zebra crossing will allow safe crossing for both pedestrians and cyclists. The western crossing has also been reviewed by Brookbanks and the expected traffic flows (see insert below) indicate that pedestrian traffic flows for the proposed units within South Marston do not require a controlled crossing, and that a zebra/parallel crossing more suitable. This is determined via a database for trip generation to identify potential pedestrian activity based on assumption of 800 homes. |
|  | Tactile paving does not appear to be laid out in accordance with ‘Guidance on the Use of Tactile Paving Surfaces.’ However, I am content that this can be resolved through the Technical Approval process. | Noted No action required |
|  | Guidance within ‘CD143’ advises that surfaced horse routes should have a minimum 2m single file width and a minimum 3m two-way width. Where there are no obvious constraints, I do not consider a 1m route to be sufficient. I would also ask that details regarding future maintenance be provided. | The horse route will be a 2m wide mown grass strip as agreed in the Strategic Design Code. |
|  | Access between the existing bridleway along Morses Lane and the new horse-riding route will require the crossing of the Primary Street, and will need to be facilitated safely. I would therefore ask that a safe crossing, which is appropriate for the anticipated level of use, is provided. | Morses Land is not a formal bridleway on the SBC definitive map. Additionally, this route has minimal levels of anticipated horse use, so the current proposed crossing point is considered sufficient, as discussed with SBC adoption officers at SBC. No action required |
| Wiltshire Archaeology (14-Mar-25) |  |  |
|  | Objection withdrawn, no further comments. | No action required |

| SMPC (17-Mar-25) |  |  |
| --- | --- | --- |
|  | We note that some of the relevant plans may not have been posted on the portal. We appear to be missing any update of ‘General Arrangements Sheet 1’. | DLA provided plans pack for SBC to verify uploaded plans. No action required |
|  | Movement Analysis - Is the applicant still working on the premise that the cycle route to the A420 for all the South Marston housing expansion is via the ‘Green Bridge over the railway line’? There are no arrangements for that route to be delivered over 3rd party land from the railway bridge to the A420. - Unless that is secured, the only possible safe cycle route to the A420 would be along the Primary Street to the Thornhill Rd junction, so should this not be widened to 5m to allow safe passage of cyclists? | The movement network has been approved through the SDC. Cyclists can utilise the Green Bridge or the existing underpass when Rowborough comes forward. No action required. |
|  | Services Corridor - Does the ducting underneath roadside cycleways have appropriate access/inspection chambers for installation, routine maintenance and upgrading of utilities? If not then the combined cycle/footpath will suffer being repeatedly dug up and patched which is unsatisfactory. | Not relevant to consideration of a planning RMA. No action required |
|  | Design of Roadside Swales/Gullies - Because the application red line does not include the relevant open space designs, there are specific instances of the Primary Street ‘under-flow’ drainage where there is no indication of how the surface water, once under the road, will reach Basin A towards Old Vicarage Lane. In other locations, the means by which surface water flows under the Primary Street is not identified. - The land slopes southwards towards the railway and the water cannot flow uphill via the Primary Street roadside filter verges. We do not understand how the notation on the plan is to be achieved given the contours of the land: ‘Existing ditchcourse to be diverted east and to connect into existing overland flow route, subject to LLFA watercourse consent’ - Our concern is that, just further west of this ‘crossing’, lies one of the areas most susceptible to flooding at the moment i.e. Morses Lane road access to South Marston Farm. The applicant should be asked to explain how this water will be captured onsite and directed safely away from access roads and housing on third party land which is the southern side of the red line in the diagram extract above. | - This detail will come forward as part of the future RMA for Phase 1 Public Open Space, which will reflect the overland flow routes identified on the approved site wide drainage strategy. No action required - The notation is in relation to the existing ditch not the roadside swales. The existing ditch currently drains north towards the properties and the overland flow route which is shown as a diversion is a shallow depression which will fall towards the existing overland flow route. The overland flow route will be re-profiled so that there is a continuous fall towards the east. - Run off from Morses Lane will be captured in the roadwide swales and primary street drainage network. Footway’s/cycleways are draining towards the road and not towards Morses Lane. Once surface water is captured within the primary street network it will be transported to the Basin A outfall at the south east corner of the site. |
|  | Drainage of FP6 Central Area (R3,4,5) - We are aware that there are new swales planned for the southern boundary of R5, it would have been helpful to show how the surface water flow reaches the planned swales that will divert it towards Basin A. | - The surface water drainage scheme has been designed in accordance with the approved site wide drainage strategy under Condition 40. No action required |
|  | Catchpit Underflow Location R6/R8 - We would assert that, given the visible impact of standing water throughout the winter to the north of the Primary Street route, the capacity of pipes, catchpit and the swale must be sufficient to avoid flooding neighbouring properties. | - Noted, drainage simulations for the primary street network have been performed with acceptable results provided. In addition the design allows for overland and exceedance flows to diver any water runoff away from development and manage in line with the FRA |